## Sheet1
* | TSG - Communal Schedule of Rates
SOR Item | Description | Unit | £
209001 | Carry out Electrical installation condition report on a Landlord’s communal parts installation of various types, compliant with Part 6 of BS7671:18th Edition and GN3. Includes all tests, client liaison, certification, safe isolation, photographic records and replacement items. Communal Block 1 to 3 Storeys | EA | 175
209002 | As 209001 but Communal Block 4 to 6 Storeys | EA | 250
209003 | As 209001 but Communal Block 7 to 12 Storeys | EA | 450
209004 | As 209001 but Communal Block 13 to 18 Storeys | EA | 522
209005 | As 209001 but Communal Block 19 to 27 Storeys | EA | 700
209006 | As 209001 but Communal Block Sheltered Accommodation | EA | 900
209007 | As 209001 but Communal Block 1 to 3 Storeys MAPS (House conversion into flats) | EA | 165
209007A | Carry out Electrical Inspection and Test to Photo Voltaic system present in accordance with to BS:EN 62446-1. | EA | 250
209007B | Access equipment required to carry out item 209007A | EA | 125
209008 | Heavy Gauge Steel Seam Welded Hot dipped inside & outside Galvanised Steel conduit to BS 4568/BSEN/IEC61386-12008. 20mm HGSW hot dipped Galvanised in &out Conduit, together with all boxes and fittings, fixed to the surface of walls, ceilings etc. (brick or concrete) with spacer bar saddles | M | 14
209009 | As item 209008 but 25mm | M | 16
209010 | As item 209008 but 32mm | M | 12
209011 | As item 209008 but 38mm | M | 6
* | Galvanised Steel Channel
209012 | Unistrut 41mm x 21mm x 2.5mm hot dipped galvanised steel channel to ASTM A123 inclusive of all spring fixings/rawlbolts, nuts and washers. | M | 11
209013 | As item 209012 but 41mm x 41mm x 2.5mm. | M | 14
209014 | Unistrut hot dipped galvanised steel channel bracket up to 300mm to ASTM A 123 coupled to 10mm galvanised threaded bar, spring fixings/rawlbolts, nuts & washers.inc paint to exposed metal. | EA | 7
209015 | 10mm galvanised steel bar | M | 5
* | Galvanised steel trunking.
209016 | 50mm x 50mm Heavy Guage ASTM A 123 hot dipped galvanised steel trunking to comply with BSEN ISO 1461:1999, inc all fixings, cutting, slotting end caps, couplers, earth links, all holes, inc builder’s holes & making good to walls & ceilings etc, touch in decs where necessary complete. | M | 15.32
209017 | 50 x 50mm hot dipped galvanised Heavy guage Steel ASTM A 123 90° bend (internal/external). | EA | 15
209018 | 50 x 50mm hot dipped galvanised Heavy guage Steel ASTM A 123 T piece. | EA | 15
209019 | 50 x 50mm hot dipped galvanised Heavy Guage Steel ASTM A 123 cross piece. | EA | 5
209020 | 50 x 50mm hot dipped galvanised Heavy Steel ASTM A123 end cap. | EA | 5
209021 | As item 209016 but 75mm x 75mm. | M | 15
209022 | 75 x 75mm hot dipped galvanised Heavy Guage Steel ASTM A 123 90° bend | EA | 15
209023 | 75 x 75mm hot dipped galvanised Heavy guage Steel ASTM A 123 T piece. | EA | 14
209024 | 75 x 75mm hot dipped galvanised Heavy Guage Steel ASTM A 123 cross piece. | EA | 5
209025 | 75 x 75mm hot dipped galvanised Heavy Guage Steel ASTM A 123 end cap. | EA | 7
209026 | As item 209016 but 100mm x 100mm. | M | 16
209027 | 100 xl00mm hot dipped galvanised Heavy Guage Steel ASTM A123 90° bend (internal/external). | EA | 15
209028 | 100 x 100mm hot dipped galvanised Heavy Guage Steel ASTM A123 T piece. | EA | 18
209029 | 100 x 100mm hot dipped galvanised Heavy Guage Steel ASTM A123 cross piece. | EA | 5
209030 | 100 x 100mm hot dipped galvanised Heavy Guage Steel ASTM A123 end cap. | EA | 5
209031 | As item 209016 but 150mm x 150mm. | M | 17
209032 | 150 xl50mm hot dipped galvanised Heavy Guage steel ASTM A 123 90° bend [Internal/External). | EA | 16
209033 | 150 x 150mm hot dipped galvanised Heavy Guage Steel ASTM A 123 T piece. | EA | 15
209034 | 150 x 150mm hot dipped galvanised Heavy Guage Steel ASTM A123 cross piece. | EA | 5
209035 | 150 x 150mm hot dipped galvanised Heavy Guage Steel ASTM A123 end cap. | EA | 6
209036 | As item 209016 but 300mm x 300mm. | M | 5
209037 | 300 x300mm hot dipped galvanised Heavy Duty Steel ASTMA 123 90° bend (internal/external). | EA | 5
209038 | 300 x 300mm hot dipped galvanised Heavy Guage steel ASTM A123 T piece | EA | 6
209039 | 300 x 300mm hot dipped galvanised Heavy Guage ASTM A123 cross piece. | EA | 6
209040 | 300 x 300mm hot dipped galvanised Heavy Guage ASTM A123 end cap. | EA | 2
* | Galvanised steel cable tray.
209041 | 50mm Heavy Duty Return Flange hot dipped galvanised Steel cable tray to ASTM A 123 and BSEN ISO 1461:1999 inc all fixings, couplers, earth links, all holes, inc builders’ holes, fire stopping & making good to walls & ceilings etc, touch in decs where necessary complete. | M | 6
209042 | 50mm hot dipped galvanised Heavy Duty Steel ASTM A 123 90° bend. | EA | 12
209043 | 50mm hot dipped galvanised Heavy Duty steel ASTM A123 T piece. | EA | 13
209044 | 50mm hot dipped galvanised Heavy DutyASTM A123 cross piece. | EA | 14
209045 | As 209041 but 100mm | M | 8
209046 | 100mm hot dipped galvanised Heavy Guage ASTM A 123 90° bend. | EA | 12
209047 | 100mm hot dipped galvanised Heavy Guage ASTM A123 T piece. | EA | 11
209048 | 100mm hot dipped galvanised Heavy Guage ASTM A123 cross piece. | EA | 11
209049 | As 209041 but 150mm | M | 9
209050 | 150mm hot dipped galvanised Heavy Guage Steel ASTM A 123 90° bend. | EA | 12
209051 | 150mm hot dipped galvanised Heavy Guage Steel ASTM A123 T piece. | EA | 13
209052 | 150mm hot dipped galvanised Heavy Guage Steel ASTM A 123 cross piece. | EA | 11
209053 | As 209041 but 300mm | M | 12
209054 | 300mm hot dipped galvanised Heavy Guage Steel ASTM A 123 90° bend. | EA | 14
209055 | 300mm hot dipped galvanised Heavy Guage Steel ASTM A 123 T piece. | EA | 11
PVC Trunking
209056 | 50mm x 50mm White PVC trunking, inc all fixings, cutting, slotting, all holes, inc builders’ holes & making good to walls & ceilings etc, touch in decs where necessary includes for every 3rd fixing or at minimum one metre intervals a fire-resistant metallic fastener | M | 9
209057 | As 209056 but 90° manufactured PVC bend. | EA | 5
209058 | As 209056 but manufactured PVCT Piece. | EA | 8
209059 | As 209056 but manufactured PVC Cross Piece. | EA | 4
209060 | As 209056 but manufactured End Cap. | EA | 2
* | Cables
209061 | Low smoke zero halogen(LSZH) insulated stranded cables to BS, EN 50525-2-41 (6491B) drawn into conduit all types. 1.5mm2 | M | 2.04
209062 | As item 209061 but 2.5mm2. | M | 2.27
209063 | As item 209061 but 4mm2. | M | 1.25
209064 | As item 209061 but 6.0mm2. | M | 1.3
209065 | As item 209061 but 10mm2. | M | 1.1
209066 | As item 209061 but 16.0mm2 | M | 1.12
209067 | Low smoke zero halogen(LSZH) insulated stranded cables to BS EN 50525-2-41 (6491B) laid into steel trunking all types. 1.5mm2 | M | 2.04
209068 | As item 209067 but 2.5mm2 | M | 2.27
209069 | As item 209067 but 4mm2 | M | 1.25
209070 | As item 209067 but 6.0mm2 | M | 1.3
209071 | As item 209067 but 10mm2 | M | 1.1
209072 | As item 209067 but 16.0mm2 | M | 1
209073 | Green/Yellow (LSZH) insulated stranded protective bonding cable to BS EN 50525-2-41 (6491B), run fixed to concrete/brickwork with appropriate clips. 4mm2 2 core & earth | M | 2
209074 | As item 209073 but 6.0mm2 | M | 5
209075 | As item 209073 but 10mm2 | M | 3
209076 | As item 2090073 but 16.0mm2 | M | 5
209077 | Low Smoke Zero Halogen Flat sheathed and insulated(XLPE/ LSZH) Twin and Earth copper cable to BS 7211.I6242B laid into existing mini trunking or clipped direct. 1.5mm2 2 core & earth | M | 6
209078 | As item 209077 but 2.5mm2 | M | 3
209079 | As item 209077 but 4mm2 | M | 3
209080 | As item 209077 but 6.0mm2 | M | 3
209081 | As item 209077 but 10.0mm2 | M | 3
209082 | As item 209077 but 16.0mm2 | M | 4
209083 | Flat LSZH BS 7211.I6242B Flat Sheated (XLPE LSZH) Three Core & earth copper insulated cables drawn into conduit. 1.5mm2 3 core and earth. | M | 7.5
209084 | Low Smoke Zero Halogen Flat sheathed & insulated (XLPE LSZH ) Two core & earth copper to BS 7211.6242B) cables fixed to any surface with appropriate clips/cable ties including 2 terminations, all holes, making good, all fire stopping and touch in decs . (Typical temporary supplies) 10mm2 2 core & earth | M | 8
209085 | As item 209084 but 16.0mm2 | M | 11
209086 | As item 209084 but 25.0mm2 | M | 14
209087 | Cu/Micatape/XLPE//LSZH/SWA/LSZH for Fire Alarm panel supplies to comply with BS 7846 & BS 5839 ONE HOUR RATING. 2 core 1.5mm2 | M | 9
209088 | As item 209087 but 2.5mm2 | M | 10
209089 | Cu/Micatape/XLPE/ /LSZH/SWA/LSZH for Fire fighting and Life Safety or increased fire risk applications to comply with BS 7846 & BS 9999 TWO HOUR RATING fixed to any surface including 2 terminations with earthing rings, cleats, shrouds, all holes, making good, all fire stopping and touch in decs as necessary. 2 core 1.5mm2 | M | 7
209090 | As item 209089 but 2.5mm2 | M | 4
209091 | As item 209089 but 4mm2 | M | 2.55
209097 | XLPE/ LSZH/SWA/LSZH BS 6724 multi-core low smoke zero halogen armoured copper cable fixed to any surface including 2 terminations with earthing rings, cleats, shrouds, all holes, making good, all fire stopping, touch in decs and test complete. 2.5mm2 2 core | M | 2.83
209098 | As item 209097 but 2.5mm2 3 Core. | M | 2.9
209099 | As item 209097 but 2.5mm2 4 Core. | M | 4.15
209100 | As item 209097 but 4.0mm2 2 Core. | M | 3.12
209101 | As item 209097but 4.0mm2 3 Core. | M | 3.29
209102 | As item 209097 but 4.0mm2 4 Core. | M | 4.95
209103 | As item 209097 but 6.0mm2 2 Core. | M | 4.02
209104 | As item 209097 but 6.0mm2 3 Core. | M | 4.3
209105 | As item 209097 but 6.0mm2 4 Core. | M | 4.41
209106 | As item 209097but 10.0mm2 2 Core. | M | 3
209107 | As item 209097 but 10.0mm2 3 Core. | M | 5.7
209108 | As item 209097 but 10.0mm2 4 Core. | M | 6
209109 | As item 209097 but 16.0mm2 2 Core. | M | 2
209110 | As item 209097 but 16.0mm2 3 Core. | M | 8
209111 | As item 209097 but 25.0mm2 2 Core. | M | 3
209112 | As item 209097 but 25.0mm2 3 Core. | M | 9
209113 | XLPE/ SWA/LSF BS 6724 multi-core low smoke zero halogen armoured copper cable laid direct into trenching. 10.00mm2 2Core | M | 3
209114 | As item 209113 but 10mm2 3 Core. | M | 5
209115 | As item 209113 but 10mm2 4 Core. | M | 6
209116 | As item 209113 but 16mm2 2 Core. | M | 3
209117 | As item 209113 but 16.0mm2 3 Core. | M | 7
209116 | As item 209113 but 16.0mm2 4 Core. | M | 6
209117 | As item 209113 but 25.0mm2 2 Core. | M | 3
209118 | As item 209113 but 25.0mm2 3 Core. | M | 8
209119 | As item 209113 but 25.0mm2 4 Core. | M | 9
209120 | TRENCHING Soft surface, dig trench 500mm deep, install 125mm Rigi-duct ducting and draw wire tape, refill trench and make good surface . | M | 35
209121 | As item 209120 but hard surface (pavement/tarmac/or the like). | M | 40
209122 | Meter to Consumer Unit 6181XY Double insulated Soft tail single core cable Cu/XLPE/PVC BS 7889 16mm2 single core Green/Yellow | M | 4
209123 | As item 209122 but 16.0mm2 Brown | M | 4
209124 | As item 209122 but 16.0mm2 Blue . | M | 4
209125 | As item 209122 but 25.0mm2 Green/yellow | M | 4
209126 | As item 209122 but 25.0mm2 Brown . | M | 5
209127 | As item 209122 but 25.0mm2 Blue . | M | 5
* | Distribution Switchgear
* | Metal clad SP&N switch fuses
209128 | 20amp S.P & N. switch fuse as EATON Excel range 15KXSC2F complete with HRC fuse link, fixings to brick or concrete and trunking, including all holes, male brass bushes and couplers, including interconnecting cable tails. | EA | 45
209129 | 32amp S.P & N. switch fuse as EATON Excel range 30KXSC2F complete with HRC fuse link, fixings to brick or concrete and trunking, including, all holes, male brass bushes and couplers, & interconnecting cable tails. | EA | 75
209130 | As item 209128 but 63amp S.P & N switch fuse as EATON Excel range 60KXSC2F | EA | 125
* | Metal Clad SP&N Switch Isolators | EA
209131 | 20amp S.P & N Switch Isolator as EATON Excel range 15AXD2 complete with holes all fixings, to brick or concrete & trunking, male brass bushes and couplers, and making good inc interconnecting cable tails. | EA | 35
209132 | As item 209131 but 32amp S.P & N switch fuse as EATON Excel range 30AXD2 | EA | 45
* | Metal clad TP&N Switch fuses
209133 | 32amp T.P & N. switch fuse as EATON Excel range 30KXTNC2F complete with all HRC fuse links, fixings brick or concrete and trunking, including all holes, male brass bushes and couplers & interconnecting cable tails. | EA | 75
209134 | As item 209133 but 63amp T.P & N. switch fuse as EATON Excel range 60KXTNC2F | EA | 185
209135 | As item 209133 but l00amp T.P & N. switch fuse as EATON Excel range100KXTNC2F | EA | 210
* | Metal Clad TP&N Isolators
209136 | 32amp T.P & N. isolator as EATON Excel range 30AXTN2 complete with al holes & making good, fixings to brick or concrete and trunking, including male brass bushes and couplers and interconnecting cable tails. | EA | 65
209137 | As item 209136 but 63amp T.P & N. isolator as EATON Excel range 60AXTN2 | EA | 75
209138 | As item 209136 but l00amp T.P & N. isolator as EATON Excel range 100AXTN2 | EA | 85
209139 | 63amp T.P & N fuse switch as EATON Glasgow range 63GNC complete with HRC fuse links, all holes, making good, fixings to brick, concrete & trunking including male brass bushes and couplers & interconnecting cable ties. | EA | 205
209140 | As item 209125 but l00amp T.P & N fuse switch as EATON Glasgow range 103GNC | EA | 198
* | Metal Clad distribution fuse boards (Landlord's)
209141 | 20amp 8 way S.P & N distribution as EATON Excel 208XSNCF complete with all HRC fuse links and fixings, to brick or concrete & trunking including male brass bushes, couplers, connections, cable tails and labels and identification of circuits. | EA | 442
209142 | As item 209141 but 20amp 12 way S.P & N distribution fuse board as EATON Excel 212XSNCF | EA | 478
209143 | As item 2091241 but 32amp 12 way T.P & N distribution fuse board as EATON Excel 312XTNCF | EA | 498
* | Bus-bar Chambers
209144 | 100amp as EATON 142 Bus-bar chamber complete with all cables, connections, labels, circuit ID, clamps and lugs, fixings to brick, concrete & trunking & test complete | EA | 85
209145 | Traffolyte engraved labels for all switch gear, fixed to the item with either nut and bolt or rivet fixing. | EA | 20
* | Fuse Replacement
209146 | In the intake cupboard carry safe out isolation installation, locate defective circuit and replace defective Distribution board 60A HRC protective device (fuse) and test complete. | EA | 50
* | MCB Replacement
209147 | In the intake cupboard carry safe out isolation installation, locate defective circuit and replace defective Distribution board TypeB MCB protective device and test complete. | EA | 65
209148 | As item 209146 except Type C MCB | EA | 65
* | RCD & Mainswitch controls
209149 | Supply & install metal clad double RCD twin socket outlet, Fixings, connections, 13amp As Crabtree range complete with surface metal box including couplers, bushes and all holes and making good. | EA | 65
209150 | Supply & install Type B/C 30mA RCBO to Consumer unit or Distribution Board | EA | 56
209151 | Supply & install 100A 30mA RCD to Consumer unit or DB. | EA | 56
* | Earth bonding installation
209152 | Supply & install BS951 bonding clamp as Tenby 12.5mm to 50mm including cleaning off pipe and connect cable and test complete. | EA | 20
2091353 | Supply and Fit adjacent to consumer unit un-insulated 4-way earth block, including warning notice& all connections & test complete | EA | 5
209154 | Supply and fit adjacent to consumer unit un-insulated 8-way earth marshalling block, including warning notice. | EA | 35
209155 | Supply and install earth pit for earth rod. | EA | 25
209156 | Supply and install 1200mm 12.5mm copper earth rod complete with clamp and cable connections & test. | EA | 16
209157 | Supply and install 2 additional lm lengths of 1200mm 12.5mm copper earth rod including ail connections | EA | 8
* | Communal Lighting
209158 | Remove existing bulkhead fitting (any non emergency type). Supply and install replacement fitting as 19 watt LED Thorlux Prismalette Luminaire, PS14914LF including all fixings, connections, holes & making good.. | EA | 148
209159 | Remove existing emergency bulkhead fitting (any type). Supply and install replacement fitting as 19 watt LED Thorlux Prismalette,TRSP14914LF self-test emergency luminaire, including all fixings, connections, holes & making good luminaires | EA | 175
209160 | Supply and install 70 Watt SON Passlight with polycarbon cover as Thorlux PL6281ZF/LMP6233, including lamp, fixings, all holes and making good & test complete. TBC by RBG CA | ITEM | 115
209161 | Supply and install 70 Watt SON Passlight with polycarbon cover and photocell as Thorlux PL6281ZFPC/LMP6233, including lamp, fixings, all holes and making good & test complete. | ITEM | 112
209162 | Supply and install 38 Watt LED Passlight (equivelant lumen output to 70W SON) with polycarbon cover as Thorlux PL14899L, including lamp, fixings, all holes and making good & test complete. | ITEM | 75
209163 | Supply and install 38 Watt LED Passlight with polycarbon cover and photocell as Thorlux P14899LPC, including lamp, fixings, all holes and making good & test complete. | ITEM | 101
* | Landlord’s Electrical Intake Cupboard Items
209164 | Supply and install MK Surface Metal Clad 13 Amp DSO with integral 30mA RCD. K6233ALM and Backbox K2213ALM including Galvanised steel containment, all fixings, holes and making good & Electrical Installation test certificate complete. test complete. | ITEM | 85
209165 | Supply and install MK 4981 WHI lighting 1 x 10A DP Grid switch & 1 x MK 4917EL WHI Emg Ltg Test Grid key switch with K3702 mounting frame plus K3492ALM Front plate plus K8891ALM Surface metal pattress box iincluding Galvanised steel trunking/conduit containment, all fixings, all holes and making good & Electrical Installation test certificate complete. | ITEM | 77
2091166 | Supply and install Designplan DQ/1400NW/XB/EM3 Quadrant black body bulkhead 16.1w LED,IP54, IK14 with integral 3 hr emergency battery luminaire including Galvanised steel containment, all fixings, holes and making good & Electrical Installation test certificate complete. test complete. | ITEM | 200
209167 | Supply and fit 300mm x 50mm x 6mm copper earth bar to BSEN 62305 (MET) mounted with removable link adjacent to incoming service head inc with warning notice. & connections to existing main earthing conductor & main protective bonding conductors and Lightning Protection system. | EA | 50
2091168 | Supply and fit BSEN ISO 7010 Rigid Plastic 450 x 600mm ‘Electric shock Resuscitation’ wall mounted notice as Stocksigns 2-2161NR | EA | 40
209169 | Supply and fit Electrical Safety rubber mat 1mx 2m to BS 921 6mm thick. | EA | 40
* | Landlords TP&N Sub-Main Distribution Boards
209170 | Isolate & remove existing unit, supply and install 9way 3phase metal clad lockable sub-main distribution board within intake or riser to existing cables/new cable installation. As XTP 9 AHS 60 A type manufactured by Ryefield Engineering Co. Ltd including fixings, backboard, terminations, fuses, cartridges, carriers and test complete including written liaison with residents and energy supplier, connect all cables and equipment to fully restore the electrical supply to each dwelling. | ITEM | 1200
209171 | Isolate & remove existing unit, supply and install 12 ways 3phase metal clad lockable sub-main distribution board within intake or riser to existing cables/new cable installation. As XTP 12 AHS 60A type manufactured by Ryefield Engineering Co. Ltd including, all labour, fixings, backboard, terminations, fuses, cartridges, carriers and test complete including written liaison with residents and energy supplier, connect ail cables and equipment to fully restore the electrical supply to each dwelling. | ITEM | 1100
209172 | Isolate & remove existing unit, supply and install 18 ways 3phase metal clad lockable sub-main distribution board within intake or riser to existing cables/new cable installation. As XTP 24 AVS 60A type manufactured by Ryefield Engineering Co. Ltd including, all labour fixings, backboard, terminations, fuses, cartridges, carriers and test complete including written liaison with residents and energy supplier, connect all cables and equipment to fully restore the electrical supply to each dwelling. | ITEM | 1100
209173 | Isolate & remove existing unit, supply and install 24 ways 3phase metal clad lockable sub-main distribution board within intake or riser to existing cables/new cable installation. As XTP 24 AVS 60A type manufactured by Ryefield Engineering Co. Ltd including, all labour fixings, backboard, terminations, fuses, cartridges, carriers and test complete including written liaison with residents and energy supplier, connect all cables and equipment to fully restore the electrical supply to each dwelling. | ITEM | 1150
209174 | Isolate & remove existing unit, supply and install 36 ways 3phase metal clad lockable sub-main distribution board within intake or riser to existing cables/new cable installation. As XTP 36 AVS 60A type manufactured by Ryefield Engineering Co. Ltd including, all labour fixings, backboard, terminations, fuses, cartridges, carriers and test complete including written liaison with residents and energy supplier, connect all cables and equipment to fully restore the electrical supply to each dwelling. | ITEM | 1195
209175 | Supply & install wooden meter board including access, all fixings, connections and liaison with the relevant electricity supply company as necessary complete. | EA | 20
209176 | Supply & install rigid PVC fuse board barrier to Ryefield fuse board (as per manufacturers recommendation). Relevant barrier sizes dependant on catalogue number of fuse board, as approved by CA. | EA | 25
209177 | Remove blown fuse and supply & install 60 Amp BS 88-3-fuse system C fuse (old BS 1361) to Ryefield board board. | EA | 30
209178 | Supply & install Henley type fuse carrier and base including all terminations and connections& test complete | EA | 25
209179 | Supply and fit appropriate electric shock hazard warning labels to distribution boards and switch gear. | A | 18
209180 | Traffolyte engraved labels for all metal clad switch gear and distribution boards, fixed to the item with either nut and bolt or rivet fixing. | ITEM | 36
209181 | Repair and make safe damaged Ryefield board door. Temporarily screw door shut using self tapping screws. Supply and install new door and lock (provide CA with spare key). | ITEM | 35
209182 | Supply and fit set of four of heat resistant oversleeves to existing single insulated meter tails. | ITEM | 12
209183 | Supply and fit to Ryefield distribution board an encapsulated A4 circuit chart in a clear PVC wallet fixed to the inside of the door. The circuit chart to indicate the dwelling each fuse serves, the rating of the protective device and the cable size and BS/ BS EN references. | EA | 22
209184 | Repair and make safe damaged/ insecure intake cupboard door/ riser. Temporarily screw door shut using either woodscrews / self tapping screws to frame. | EA | 15
209185 | Supply and fit new lock to Ryefield distribution board (provide CA with spare key). | EA | 35